## Slide 1
DOORS AND HARDWARE FOR HEALTHCARE
march 12, 2020 | spring seminar |
PRESENTERS:
Greg Meyer AIA, LEED AP Architect Flad Architects
Ramon Moll AIA, NCARB Architect
Flad Architects

## Slide 2
Understand the fire and smoke requirements for door openings in relationship to location.
Understand the requirements for doors in the means of egress and options for securing them for the health, safety, and welfare of the patients.
Be able to integrate door requirements of the various doors into the project.
Be able to develop a correct program of testing and maintenance for the doors that will be installed in the project.
Learning Objectives

## Slide 3
Doors and Hardware for Healthcare
p 3

## Slide 4: Hartford Hospital, Connecticut – 1961

## Slide 5: Hartford Hospital Fire – 1961

## Slide 6: Hartford Hospital Fire – 1961

## Slide 7: Hartford Hospital Fire – 1961

## Slide 8: Hartford Hospital Fire – 1961

## Slide 9: Hartford Hospital Fire – 1961 Richard Trejarian

## Slide 10: Hartford Hospital Fire – 1961

## Slide 11: Hartford Hospital Fire – 1961
"We are going to investigate this, and we are going to change the way that hospitals are built.” Dr. Steward Hamilton

## Slide 12
The disaster prompted changes nationwide in hospitals and building codes
Lessons Learned from the Hartford Fire:
Doors, and hardware play a critical role achieving and maintaining Life Safety. In the Hartford fire, those who stayed in rooms with closed doors survived the fire.
Any Hallways greater than 20 feet must have an exit door. This is to recognize the importance of the appropriate number of exits in the means of egress. In Hartford, people were trapped in the south wing with no way out.
Hospital must have automatic sprinklers protection. In Hartford only the hazardous areas and storages had sprinkler systems.
Fire compartmentalization has been further developed with more efficient wall separation.
Re-evaluation of the cross-corridor door in smoke compartments. Current code standards require double egress. In the 1961, it was one big 8-foot door with no opportunity to egress once closed.
All patient doors must have positive latching

## Slide 13: Code Reference Material
Codes that we will reference in this presentation include:
North Carolina State Building Code (NCSBC) 2018
North Carolina State Building Code Fire Prevention Code, 2018, NFPA 101, 2015 Life Safety Code, and other codes and standards
National Fire Protection Association (NFPA) 80, Standard for Fire Doors and Other Opening Protectives
NFPA 105, Standard for the Installation of Smoke Door Assemblies and Other Opening Protectives
UL 1784 Standard for Air Leakage Test of Door Assemblies and other Opening Protectives
Photo credit: ANSI Blog

## Slide 14: Life Safety Plans

## Slide 15: Life Safety Plans
Fire/smoke compartments
Occupant load and exit width
Means of egress
Exit signage
Sprinklered areas
Fire extinguisher locations

## Slide 16: Life Safety Plans – Diagram
FIRE & SMOKE PROTECTION FEATURES

## Slide 17: Door Hierarchy – Non-Rated Door within Suite (Room)
A
FIRE & SMOKE PROTECTION FEATURES
NON-RATED DOOR WITHIN SUITE (ROOM)
A

## Slide 18
B
Door Hierarchy – Corridor Door, 0 HR. Smoke Partition
FIRE & SMOKE PROTECTION FEATURES
CORRIDOR DOOR
B

## Slide 19
B1
Door Hierarchy – Corridor Door, 0 HR. Smoke Partition
FIRE & SMOKE PROTECTION FEATURES
CORRIDOR DOOR UNEQUAL PAIR
B1

## Slide 20
B2
Door Hierarchy – Corridor Door, 0 HR. Smoke Partition
FIRE & SMOKE PROTECTION FEATURES
CORRIDOR DOOR
B2

## Slide 21
B3
Door Hierarchy – Patient Toilet Door, Non-rated Partition
FIRE & SMOKE PROTECTION FEATURES
SLIDING DOOR PATIENT TOILET
B3

## Slide 22
B4
Door Hierarchy – Corridor Door, 0 Hr. Smoke Partition
FIRE & SMOKE PROTECTION FEATURES
SLIDING ICU CORRIDOR DOOR
B4

## Slide 23
B5
Door Hierarchy – Corridor Door, 0 Hr. Smoke Partition
FIRE & SMOKE PROTECTION FEATURES
CORRIDOR DOOR OPERATING ROOM
B5

## Slide 24
C
Door Hierarchy – Corridor Door, 0 Hr. Smoke Partition
FIRE & SMOKE PROTECTION FEATURES
ELEVATOR LOBBY
0 HR. SMOKE PARTITION
C

## Slide 25
D
Door Hierarchy – Cross Corridor, 1 Hr. Smoke Barrier
FIRE & SMOKE PROTECTION FEATURES
CROSS CORRIDOR SMOKE BARRIER DOOR
(SMOKE COMPARTMENT)
D

## Slide 26
E
Door Hierarchy – ⅓ Hr. Fire Doors, 1 Hr. Fire Barrier
FIRE & SMOKE PROTECTION FEATURES
20 MIN. FIRE DOOR
IN SMOKE BARRIER
(SMOKE COMPARTMENT)
E

## Slide 27
F
Door Hierarchy – 1½ Hr. Fire Doors, 2 Hr. Fire Barrier (Exit)
FIRE & SMOKE PROTECTION FEATURES
90 MIN. FIRE DOOR
AT STAIRWELL
F

## Slide 28
F1
Door Hierarchy – Fire Doors in a 1 Hr. Fire Barrier
FIRE & SMOKE PROTECTION FEATURES
FIRE DOOR
F1

## Slide 29
F2
Door Hierarchy – 45 Min. Fire Door in Smoke Barrier
FIRE & SMOKE PROTECTION FEATURES
45 MIN. FIRE DOOR
IN SMOKE BARRIER
F2

## Slide 30: NFPA 80 – Requirements
NFPA 80 (2010) 4.8.4 Clearance
4.8.4.1 The clearance under the bottom of a door shall be a maximum of ¾ in. (19 mm).
4.8.4.2 Where the bottom of the door is more than 38 in. (965 mm) above the finished door, the maximum clearance shall not exceed 3/8 in. (9.5 mm) or as specified by the manufacturer’s label service procedure.
NFPA 80 (2010) 6.3.1.7* Clearances
6.3.1.7.1 The clearances between the top and vertical edges of the door and the frame, and the meeting edges of doors swinging in pairs, shall be 1/8 in. ±1/16 in. (3.18 mm ±1.59 mm) for steel doors and shall not exceed 1/8 in. (3.18 mm) for wood doors
6.3.1.7.2 Clearances shall be measured from the pull face of the door(s).
Door Material | Top / Vertical / Meeting Edge | Bottom
Wood | 1/8 inch | 3/4 inch
Steel | 1/8 inch (± 1/16 inch) | 3/4 inch

## Slide 31
Door Inspection and Maintenance
Top Reasons for LS.02.01.10 and LS.02.01.30 Door Failures
Latch failure
Rating/label
Closer missing
Gap/undercut
Hardware
Blocked
Damaged
Jerry-rigged
Door missing
Louver
Roller latch
Joint Commission findings related to fire-door maintenance. Graphic courtesy of the American Society for Health Care Engineering.
100
200
300
400
500
600
700
800
860
343
342
336
304
137
112
49
12
11
8

## Slide 32
H
Door Hierarchy – Exterior Doors
FIRE & SMOKE PROTECTION FEATURES
EXTERIOR PAIR OF DOORS
H

## Slide 33
H1
Interior Courtyards – Exterior Doors, Means of Egress
FIRE & SMOKE PROTECTION FEATURES
EXTERIOR PAIR OF DOORS AT COURTYARD (INSWING)
H1

## Slide 34
H2
Door Hierarchy – Exterior Door, Exit Discharge
FIRE & SMOKE PROTECTION FEATURES
EXTERIOR DOOR EXIT DISCHARGE
H2

## Slide 35
D
Door Technology – Cross Corridor Door, Access Controlled
FIRE & SMOKE PROTECTION FEATURES
CROSS CORRIDOR DOOR ACCESS CONTROLLED
D

## Slide 36
D
Door Technology – Cross Corridor Door, Delayed Egress
FIRE & SMOKE PROTECTION FEATURES
CROSS CORRIDOR DOOR DELAYED EGRESS
D

## Slide 37
D
Door Technology – Cross Corridor Door, Special Egress
FIRE & SMOKE PROTECTION FEATURES
CROSS CORRIDOR DOOR SPECIAL EGRESS
D

## Slide 38: Re-Entry from Stairwell
1
2
3
4
5
6
7
8
9
10
11
RE-ENTRY POINT
RE-ENTRY POINT
RE-ENTRY POINT
Stairwell Re-entry
2012 NFPA 101
Stairs serving 4 stories or less can be mechanically locked from the stair side.
Locked stair doors must be automatically released upon activation of the fire alarm system.
NCSBC 2018
403.5.3 Doors locked on the stair side must be capable of being simultaneously unlocked without unlatching from the fire command center or a signal by emergency personnel from a single location inside the main entrance to the building.
403.5.3.1 High-Rise buildings require two–way communication system
Specify fail-safe electrified locks to ensure doors (where required) will be unlocked in the event of power loss.

## Slide 39: Hartford Hospital Fire – 1961
"We are going to investigate this, and we are going to change the way that hospitals are built.” Dr. Steward Hamilton

## Slide 40
Nancy Coniglione, patient
Henrietta Conover, visitor
Jennie Dunn, patient
Adelene Fainter, visitor
C. Frederick Greenleaf, patient
Laura Greenleaf, visitor
Grace Hatch, employee
Dr. Norman Hedenstad, resident physician
Gladys Kokaska, patient
Ruth LaPenta, patient
Theresa Mascaro, visitor
Diane Pape, patient
Angeline Seigel, visitor
Charles Seigel, patient
Sadie Ward, employee
Marion Winget, nurse
In memory of

## Slide 41: Hartford Hospital, Connecticut – 1961

## Slide 42
DOORS AND HARDWARE FOR HEALTHCARE
march 12, 2020 | spring seminar |
PRESENTERS:
Greg Meyer AIA, LEED AP Architect Flad Architects
Ramon Moll AIA, NCARB Architect
Flad Architects
Thank you!